Exhibit B     EXHIBIT B

Scope of Work

138883 – Cemetery Sun, LLC

24638 Adams Rd, Frederick, IL

4.975 MW (AC) Distributed Generation Solar Plant

Table of Contents

Solar Plant	3

Milestone Definitions	3

Proposed Activity Schedule- Non-Binding (guaranteed completion date prevails)	4

Contractor Scope and General Conditions (applies to all scopes)	5

Site Civil Services (applies to civil scope only)	7

Foundation Installation Services (applies to foundation/mechanical scope only)	9

Racking Installation Services (applies to racking/mechanical scope only)	10

Tracker Installation Services (applies to racking/mechanical scope only)	11

Module Installation Services (applies to module/mechanical scope only)	11

Electrical Services and Material (applies to electrical scope only)	12

Medium Voltage Services and Materials (applies to MV/Electrical scope only)	15

Fencing Services and Materials (applies to fencing scope only)	16

Landscaping Services and Materials (applies to landscape scope only)	17

Company Provided Services and Materials	17

Other Contractor Requirements	18

Quality Control	18

Contractor Project Contacts	18

Project Site Access and Security	18

Work Plan and Schedule	18

Inspection	19

Material Receiving, Handling, Inventory & Reporting	19

Safety	20

Documentation	21

Fire Prevention	21

Severe Weather	21

Winter Conditions Contingency	22

Company Contacts	23

Exhibit 1. Furnish & Install (F&I) Schedule	24

Exhibit 2. Execution Plan	25

Exhibit 3. Alternate and Unit Price (as applicable to your scope only)	27

Exhibit 4. Bid Quantity Breakout (as applicable to your scope only)	28

Exhibit 5. Owner Provided Equipment Schedule	29

Scope of Work

# Solar Plant

Cemetery Sun, LLC (the “Owner”) is entering into an Engineering, Procurement, and Construction Contract (“EPC Contract”) with Nexamp, Inc. (“Nexamp” or the “Company”), for services related to the design, construction and placement into operation of one solar photovoltaic electric generating system and related ancillary equipment with a nominal capacity of 4.9 MW (AC) in accordance with the EPC Contract (the “Project”). The Project is located at 24638 Adams Rd, Frederick, IL (the “Site”) as further detailed in the Project Agreement.

The Company is to provide construction and installation services to build the Project. The Company may enter one or more subcontracts with respect to any item or portion of the Project, as defined in the EPC Contract. Nexamp is engaging  Subcontractor (as used in this Scope of Work, the “Contractor”) will be responsible for all work, as described in this Exhibit B to the Project Agreement Scope of Work (“SOW”) and any Change Orders related to this SOW, for providing labor, materials, components, equipment, tools, transportation, trade equipment, and other facilities and services that are necessary for the proper execution, construction, testing, and completion of the Project. All Services as defined in the Project and Subcontractor Agreements and Contractor’s obligations under this SOW includes, activities, materials, and components related to the construction, installation, and management of the Project, shall for purposes of this SOW be referred to as the Work (the “Work”). Any capitalized terms used herein that are undefined shall have the meaning ascribed to them in the Project and/or Subcontractor Agreements, and to the extent any definitions are in conflict, shall control unless specifically stated otherwise.

# Milestone Definitions

| Certificate of Completion (“COC”) | Utility form that is issued by the local inspector and provided to the Utility. |
| --- | --- |
| Guaranteed Completion | Physical aspects of the project have been fully constructed, all major equipment has been installed per the applicable Drawings and Specifications, draft record set has been submitted to Nexamp, and COC has been provided. All Commissioning Documents have been submitted for approval by Nexamp. |
| Mechanical Complete | Project has achieved Construction Completion and all Commissioning documents have been approved by Nexamp. |
| Witness Test | Site has achieved Mechanical Completion, Nexamp has provided approval to conduct a Utility Witness Test, and Utility can safely conduct inspection and verify system operation. |
| Permission To Operate (PTO) | Once the project has successfully passed a Witness Test, the Utility then issues their permission to operate, and the system can then be turned on and interconnected to the grid. |
| Substantial Completion | All work related to the Scope of Work is complete and punchlist has been agreed upon. |
| Final Completion | Punchlist is complete, all permits are closed, final unconditional lien waivers have been submitted. |
| Guaranteed Completion Date | The date that Subcontractor must have all the Services and Deliverables completed as set forth in and in accordance with this Scope of Work by the date set forth in Section 4 of the Project Agreement. (Construction Complete) |
| Drawings | Any and all drawings related to the System’s design and specifications, including all architectural, civil, engineering, environmental, As-Build drawings, IFC drawings, and any other drawings or designs provided under this Scope of Work. |

# Proposed Activity Schedule- Non-Binding (guaranteed completion date prevails)

| Activity | Completion Date |
| --- | --- |
| Build Access Road | May 1st – May 7th, 2026 |
| Racking Installation | June 11th – July 9th, 2026 |
| Module Installation | June 25th – July 23rd, 2026 |
| LV Trenching and Conduit Install | May 11th – May 22nd, 2026 |
| MV Trenching and Conduit Install | June 9th – June 22nd, 2026 |
| Equipment Pad Prep | May 11th – May 22nd, 2026 |
| Concrete Form, Pour, Cure | May 27th – June 16th, 2026 |
| Equipment Installation | May 26th – June 30th, 2026 |
| Medium Voltage Installation | May 11th- June 25th, 2026 |
| Fence Installation Start | May 13th – May 27th, 2026 |

# Contractor Scope and General Conditions (applies to all scopes)

- Contractor shall provide equipment, labor, and materials necessary to deliver the installation of the solar photovoltaic (“PV”) system and other services, as provided herein, pursuant to the Drawings set forth in Exhibit Q of the Project Agreement, and documents listed in the bid package. Contractor shall supervise and direct the construction means, methods, techniques, sequences, and procedures as well as coordinate and oversee all on site activities and deliveries including unloading/unpacking of necessary to satisfy the contract and any required conditions of contractor pulled permits.

- Unless specified otherwise all materials and workmanship shall be in accordance with federal, state and local regulations, specifications of highways and bridges at last revisited, the governing town Public Works Department and or appropriate local authorities, including but not limited to Planning and/or Zoning Board decisions and Conservation Commission Order of Conditions (“OOCs”) (or equivalent jurisdictional requirements, as applicable), commissions, boards, agencies, or regulatory authorities having oversight of the Owner, the Company, the Project, or the Site.

- Any changes or substitutions from Nexamp contract Drawings and specifications during bid process must be clearly noted in writing and attached as part of the bid. Excluding anything requested without signed acceptance by a Nexamp Manager will be considered part of the scope of work.

- Submission of the bid documents shall serve as evidence that the contractor is familiar with all contract documents referenced in the documents section, site conditions and premises. Failure by the Contractor to consider contract documents, site conditions, and premises shall in no way relieve the contractor of obligations relating to the bid proposal or contract.

- Contractor shall use track vehicles, when possible, within the array to minimize damage to site work. Contractor shall be responsible for damage incurred during construction to the Site. This includes but not limited to; wetland remediation work, Storm Water Pollution Prevention Plan (“SWPPP”) drainage, solar mounting equipment, and or security fences.

- Contractor shall maintain on site “Red Line” As-Build construction Drawings, to be updated weekly and to be reviewed by Nexamp. Contractor shall provide As-Build construction Drawings prior to Guaranteed Completion Date.

- Contractor shall submit specification sheets on all materials intended for use at a minimum of seven (7) days prior to the notice to proceed, unless otherwise approved by Nexamp.

- Contractor Requests for Information to Nexamp must include suggestive solution when possible.

- All work must be completed in accordance with current Nexamp Specifications (Electrical and Civil), Drawings, installation manuals, and Authorities Having Jurisdiction (“AHJ”) requirements. Contractor shall be responsible for scheduling and coordinating all necessary Site and workmanship inspections, surveys, or tests.

- All Work must comply with the conditions of the stormwater permit.

- Contractor is required perform the Work in such a manner that complies with SWPPP permit requirements at all times. Rutting or damage to Site needs to be mitigated/remediated as soon as possible to minimize safety risks and potential soil runoff from the site.

- Contractor shall be responsible for storage and security of their materials and equipment. Security will not be provided for Contractor’s property by Owner or Nexamp.

- Contractor shall maintain general housekeeping throughout the duration of the work and shall leave the Site and surrounding areas in a generally neat and clean condition, free of trash, at the end of each workday (and upon completion of all Work and/or expiration or termination of this SOW). This includes, but not limited to, sediment in roadways, the construction entry free of debris, and/or as otherwise directed by Nexamp or applicable laws and regulations.

- Contractor shall adhere to the Nexamp recycling program and procedures at all times throughout the performance of the Work.

- Contractor shall coordinate with all other trades and other of Nexamp’s contractors and agents working on Site prior to and during construction as required for all parties to complete the Work (the same shall be required of them).

- Construction means and methods shall comply with all OSHA safety requirements. All Contractor employees (including from any Lower-Tier Subcontractor) on Site must have at minimum OSHA 10-hour certification. A working, Class C fire extinguisher shall be supplied and maintained at each work area.

- Laydown areas shall be coordinated by Nexamp and determined prior to the start of construction.

- Contractor shall provide allowance for severe weather conditions in accordance with the inclement weather plan as referenced below.

- Contractor shall be responsible for temporary lighting, temporary power, extension cords, barriers, fall protection, or other means necessary to meet OSHA and Nexamp safety standards to provide a safe and satisfactory work environment for their scope.

- Contractor shall be responsible for coordinating inspections for permits that they obtained and cover any costs associated with these inspections by any authorities having jurisdiction over the Project to obtain final permit inspection and sign-off.

- Contractor shall complete all Work associated with Project, including billing and information reporting on or within the allotted Project Schedule.

- Contractor to handle all deliveries that are noted on the Furnish and Install Schedule (F&I for their scope), in a safe, neat, and orderly manner.

- Contractor shall provide a two-year workmanship warranty, which shall begin upon Nexamp’s receipt of the Certificate of Compliance.

- If the project complies with the Inflation Reduction Act and, or an applicable state program as set forth in the Project Determination Summary the Workforce Requirements as more specifically defined in the Project and Subcontractor Agreements.

- In the event that the Contractor begins to fall behind on milestone schedules, the Company reserves the right to require Contractor to submit a recovery schedule which outlines the strategies and measures that the Contractor project team intends to take to bring the Project back on schedule. Recovery schedule shall be submitted by the Contractor within 48 hours of Company’s request.

- Contractor shall remediate all open observations and provide notification to Company of completion fifteen (15) working days after Construction Completion.  Nexamp employee shall verify remediation of all observations.  Failure by Contractor to address any open observations may result in Company withholding 150% of the value of costs associated with remediation of open items.  The value of remediation shall include material, labor and associated overhead costs.

- Owner supplied punch list may be presented via Procore after Mechanical Completion, Contractor shall be responsible for the remediation within fifteen (15) working days after receipt.

- As set forth in this Scope of Work or the Project Agreement, Contractor shall apply for all necessary permits for their scope (typically electrical) as required by the authority having jurisdiction necessary to complete all work according to the contract documents. All permitting fees and associated costs shall be included in Contractor’s bid proposal and not a passed through cost to Nexamp for payment.

- All contractors shall ensure that their activity does not go beyond the limits of disturbance and must not encroach on neighboring property. If unsure of LOD, confirm with Nexamp PM or site supervision. Do not use neighboring property to access the site at any time for any reason.

## Site Civil Services (applies to civil scope only)

- Contractor shall provide all general conditions necessary to support work including, but not limited to site supervision, quality assurance, safety inspections, storage, and office trailers (if needed), power and lighting (if needed), police details (if needed), AHJ required signage (traffic control, etc.), and equipment needed to complete the Work.

- Contractor shall maintain general housekeeping throughout the duration of its performance of the Work and leave the Site and surrounding areas, including public roadways and Site entrance, in a generally neat and clean condition, free of trash, at the end of each workday.

- Contractor responsible for contacting DIG SAFE and providing the corresponding ticket number to Nexamp prior to mobilization on Site.

- Contractor adhere to SWPPP, in accordance with the Environmental Protection Agency Construction General Permit. Nexamp shall monitor the Site after the site contractor’s major activities have ceased and the electrical contractor has assumed control of entire Site. Contractor’s bid proposal shall include costs for returning to the site periodically to make repairs as required through Project completion. Contractor’s bid proposal shall additionally include interim measures necessary to control storm water during construction.

- Contractor shall be responsible for all items included in the SWPPP including but not limited to, naming a responsible person, participating in preconstruction meeting prior to the start of any new work process, and daily inspections while on Site. Contractor’s bid proposal shall additionally include five (5) mobilizations to repair erosion control barriers and maintain rip rap swales, basins, and ponds after de-mobilization and until the Project has reached Notice of Termination (“NOT”) from the AHJ.

- Retainage shall be released after all punchlist items have been resolved, site is stabilized, and submission of the NOT to Nexamp. Discuss with the Nexamp Project Manager as needed.

- Contractor shall provide dust control and street sweeping throughout the Site, as required.

- Contractor’s bid proposal shall include all other Erosion Control Barriers to maintain the Site as required by SWPPP and OOCs (or equivalent jurisdictional requirements, as applicable).

- Contractor’s bid proposal shall include one (1) full stabilization seeding after completion of earthmoving work, and one (1) partial stabilization seeding at the completion of the electrical work. All disturbed areas should be included. Additionally include grading out ruts and final array treatments upon completion of all construction.

- Contractor shall provide electronic and hard copy As-Build Drawings prior to Project completion date. This is to be included in the Contractor’s cost.

- Contractor shall submit specification sheets on all materials intended for use, seven (7) days prior to the start of construction.

- Contractor shall include at their cost construction and installation of a project job board, as well as 2’ X 3’ Department of Environmental Protection sign. Contractor shall also include any additional signs to satisfy the SWPPP and OOCs (or equivalent jurisdictional requirements, as applicable) requirements.

- Contractor shall include in their cost one (1) tree clearing mobilization for tree clearing if required.

- Civil Contractor should include two (2) mobilizations for vegetative maintenance mowing at the discretion of Nexamp. The 1st to be completed prior to solar foundations being surveyed and installed, and the 2nd to be completed prior to Project handover to Owner.

## Foundation Installation Services (applies to foundation/mechanical scope only)

Contractor will assemble, construct, and install with its own forces and/or with Lower-Tier Subcontractors the following Work in accordance with the Project and Subcontractor Agreements.

Contractor shall provide the following, but not limited to, material that is UL and 2017 National Electric Code (“2017 NEC”) compliant or as designated on the construction drawings.

- All such equipment or assemblies requiring torque shall be correctly torqued and marked with red to designate status of having been torqued. Failure of a bolt having been designated and marked as torqued may require all assemblies to be re-torqued in the presence of a Company Supervisor, if Contractor fails to remedy within seventy-two (72) hours.

- All installation and construction shall be performed in accordance with manufacturer requirements, installation manuals, and design IFC Drawings, and shall comply with the requirements for the maintenance of all warranties set forth in the Equipment Specification.

- Contractor shall be responsible for all rigging and logistics necessary to get all materials into place.

- Contractor shall be responsible for all actions of the surveyor, whether a Contractor employee or a Lower-Tier Subcontractor for their scope. Surveyor’s must show up on Site with working equipment, the latest design and CAD files.

- Contractor shall forecast and provide the equipment, labor and material to meet schedule provided in Project request for proposal.

- Contractor shall ensure that all sunken excavations in and around foundations are back filled with proper aggregate at time of installation as well as during workmanship warranty period.

- Contractor to install the combiner boxes, weather station(s), camera pole, string inverter, and inter-row conduits support posts per the structural Drawings included in the IFC Drawings.

- Contractor to first construct a “Golden Row” for inspection by Nexamp Quality Assurance and Quality Control (“QA/QC”) prior to construction of the remaining array. Closure of the Golden Row inspection does not supersede Nexamp’s Technical Specifications. Company will require the Contractor to change array installation/wire management techniques during construction to ensure approved “Golden Row” Specifications are met.

- Contractor shall perform quality assurance checks on pile foundations (or any type of solar foundations) as they are being installed and make corrections in real time.

- Contractor shall keep a log of all pile refusals. The log must include row number, location in row, photos, and remediation status. The log must be submitted to Nexamp at least five (5) Business Days prior to redline submissions.

- Should the installation be delayed through no fault of the Company, Contractor shall be responsible for assuming cost of delay from all effected parties (Engineer, Construction Supervisor, etc.) if Company incurs any change orders, including any Delay Liquidated Damages as set forth in the Project and Subcontractor Agreements.

- Contractor has confirmed if the project requires “yellow jacket” installation and has included this cost in their proposal. If contractor is unsure, please consult with the Nexamp project manager prior to submitting your proposal.

## Racking Installation Services (applies to racking/mechanical scope only)

- Contractor shall build all racks in accordance with design standards and shall be responsible for feathering of all racking to ensure rack is built within design tolerance and has a uniform and continuous leading edge as permissible.

- Contractor shall make efforts to minimize damage to site grading by vehicles on Site.

- Contractor shall ensure mounting dunnage including pallets and cardboard is maintained in a clean and orderly fashion until removed from site for recycling.

- Contractor shall submit the commissioning document A-RAC Racking Torque Certifications REV_D no later than the Guaranteed Completion Date.

- Contractor to first construct a “Golden Row” for inspection by Nexamp Quality Assurance and Quality Control (“QA/QC”) prior to construction of the remaining array. Closure of the Golden Row inspection does not supersede Nexamp’s Technical Specifications. Company will require the Contractor to change array installation/wire management techniques during construction to ensure approved “Golden Row” Specifications are met.

## Tracker Installation Services (applies to racking/mechanical scope only)

- Tracker commissioning must be completed by Electrical and/or Mechanical Contractors. Contractor shall reference the Procore Documents Tool for the manufacturer’s installation manual regarding commissioning requirements for the specific tracker.

- High Wind/Snow Load Stow – The tracker must be stored daily in the correct orientation (per install manual/manufacturer direction/spec) before leaving site.

- All current installation manuals and row box keys/weather stations keys inventoried and stored indoors (Connex Box) per the manufacturer’s requirements.

- Contractor shall offer support during the commissioning and live tracking of the rows to ensure no defects in workmanship or materials are present with the system. This includes the Nexamp commissioning documents and any manufacturer’s commissioning procedures.

- If network controller is not operational at time of Golden Row, through no fault of the Company or Company’s other Contractors, Contractor to provide mechanical sign off to continue with module installation.

- Contractor to first construct a “Golden Row” for inspection by Nexamp Quality Assurance and Quality Control (“QA/QC”) prior to construction of the remaining array. Closure of the Golden Row inspection does not supersede Nexamp’s Technical Specifications. Company will require the Contractor to change array installation/wire management techniques during construction to ensure approved “Golden Row” Specifications are met.

## Module Installation Services (applies to module/mechanical scope only)

Contractor shall assemble, construct, and install with its own forces and/or with Lower-Tier Subcontractors the following Work in accordance with the Project and Subcontractor Agreements.

Contractor shall provide the following, but not limited to, material that is UL and 2017 2017 NEC compliant or as specified in the drawings.

- Contractor shall make efforts to minimize damage to site grading by vehicles on Site.

- Contractor shall ensure module dunnage including pallets and cardboard is maintained in a clean and orderly fashion until removed from the Site for recycling by Contractor. Contractor shall dispose of all other Project waste at a certified recycling center.

- Any damaged modules, whether from shipping or by Contractor (or its Lower-Tier Subcontractors’) personnel’s actions, must be reported to Company. Modules damaged by Contractor (or its Lower-Tier Subcontractors) may be back charged to the Contractor as a credit Change Order, depending on the circumstances.

- Contractor shall submit commissioning document A-MOD Racking Torque Certifications REV_C no later than the Construction Compete milestone date.

- Contractor to first construct a “Golden Row” for inspection by Nexamp Quality Assurance and Quality Control (“QA/QC”) prior to construction of the remaining array. Closure of the Golden Row inspection does not supersede Nexamp’s Technical Specifications. Company will require the Contractor to change array installation/wire management techniques during construction to ensure approved “Golden Row” Specifications are met.

- Should the installation be delayed through no fault of the Company, Contractor shall be responsible for assuming cost of delay from all effected parties (Engineer, Construction Supervisor, etc.) if Company incurs any change orders, including any Delay Liquidated Damages as set forth in the Project and Subcontractor Agreements.

## Electrical Services and Material (applies to electrical scope only)

Contractor shall assemble, construct, and install with its own forces and/or with Lower-Tier Subcontractors the following Work in accordance with the Project and Subcontractor Agreements.

Contractor shall provide the following, but not limited to, material that is UL and 2017 NEC compliant or as specified in the drawings.

- Contractor shall include material and labor costs based on the F&I schedule. Contractor shall include labor, materials and equipment cost for off-loading and installation of all Nexamp and Contractor supplied materials for electrical scope without limitation. Contractor shall include receiving all inventories and assume liability for all material delivered to the Site. Contractor shall notify Nexamp within 24 hours of receipt of any deficiencies and/or damages.

- Contractor shall include all medium voltage (“MV”) work. Nexamp will provide MV equipment in accordance with the F&I schedule. All other MV equipment shall be provided by Contractor.

- Contractor shall provide an MV Bucket Truck and electrical support (Utility Interconnection Support) on Site the day of the Nexamp approved Witness Test date with the local utility. Nexamp to provide confirmed Utility Witness Test date at least three (3) business days prior.

- Contractor shall ensure all dunnage including pallets and cardboard is maintained in a clean and orderly fashion until removed from the Site for recycling. All other Project waste shall be disposed of at a certified recycling center, Nexamp’s dumpsters shall be used for all refuse created by all contractors on Site and must remain on Site until final punchlist is completed.

- Contractor shall provide all general conditions necessary to support work, including but not limited to site supervision, safety inspections, quality control, temporary toilets, storage, office trailers, and all other related tools, equipment, ordinarily and customarily supplied by Contractors performing the same or similar Work in the applicable location. Contractor shall also include securable, furnished office space for Owner/Nexamp employees, drinking water, etc. The Nexamp trailer shall be mobilized once the Site Contractor has made a staging area available, even if prior to mobilization of its Work and shall remain on Site until completion of final punchlist, unless otherwise authorized by a Nexamp Manager.

- Contractor shall provide temporary electrical power (and final disconnects) to the Nexamp supplied job trailer, upon schedule and request, for the duration of the Project schedule.

- Contractor shall be responsible for securing and payment of electrical permit and scheduling/coordinating all related inspections. A copy of these permits shall be provided to Nexamp prior to mobilization when applicable.

- Contractor shall coordinate with the foundation, mechanical, and other contractors on Site on all underground conduit/conductors and trenching. Trenching may need to be adjusted to avoid the PV system racking foundations.

- Contractor to install the combiner boxes, weather station(s), camera pole, string inverter, and inter-row conduits support posts per the structural Drawings included in the IFC Drawings.

- Contractor shall not attempt to operate the PV system.

- Contractor shall be present for all QA/QC inspections and system commissioning, including energization/interconnection.

- Contractor shall conform to Journeymen/Apprentice ratio per the Project Determination Summary.

- Contractor shall remediate all open punchlist items and provide notification to Company of completion within ten (10) working days of Mechanical Completion. Nexamp employees shall verify remediation of all punchlist items. Failure by Contractor to address any open punchlist items may result in Company withholding 150% of the value of costs associated with remediation of open punch list items, in addition to any Delay Liquidated Damages should Contractor fail to meet the Guaranteed Completion Date. The value of remediation shall include material, labor, and associated overhead costs.

- No devices shall be mounted such that they cast a shadow on any PV module.

- All wiring and raceways shall be protected and secured from potential damage, especially in areas where wiring runs may otherwise be accessible. Contractor shall take reasonable measures to protect such wiring from wire on metal contact, vandalism, and unintentional damage (e.g. sharp edges.).

- Contractor shall install pad mount transformers, inverters, switchgear, panel boards, relays, Data Acquisition System (“DAS”), and all equipment as indicated on the Drawings per specifications and plans.

- Contractor shall correctly torque all such equipment or assemblies requiring torque, and mark torqued bolts to designate status of having been torqued. Failure of a bolt having been marked and designated as torqued may require all assemblies to be re-torqued in the presence of a Company Supervisor, if Contractor fails to remedy within seventy-two (72) hours. Nexamp reserves the right to source a third party to meet torquing requirements for which the Contractor will be held responsible for costs incurred if Contractor fails to remedy within seventy-two (72) hours after written notice.

- Contractor shall perform the installation and construction in accordance with all manufacturer’s requirements, installation manuals, and design Drawings in order to comply with the requirements for the maintenance of all warranties set forth in the Specification. Nexamp will, as applicable and when necessary, provide installation manuals relevant to the Services Contractor is performing.

- Contractor shall be responsible for all rigging and logistics necessary to get all materials into place. One (1) day of crane work shall be included in Contractor’s bid proposal. If additional days are needed due to Company delays in providing materials, the Company will be required to pay for additional direct costs to the extent it caused the delay.

- Contractor shall be responsible for DAS wiring and commissioning support, weather station and pyranometer installation, string inverter programming, and combiner box mapping, in conjunction with the Nexamp Operations Center.

- Contractor shall complete all commissioning testing and associated reports in accordance with the electrical Specifications and the commissioning testing criteria included in Exhibits P and J of the Project Agreement, respectively. This includes, but is not limited to, exact date of calibration, insulation resistance testing at the correct voltage (1,000 – 1500 – 2000) meter testing (per Exhibits P and Q of the Project Agreement), fall of potential tester, IV curve tracer (utilizing approved testing equipment – ex., Solmetric PV Analyzer), and certified torque wrenches.

- Contractor to first construct a “Golden Row” for inspection by Nexamp Quality Assurance and Quality Control (“QA/QC”) prior to construction of the remaining array. Closure of the Golden Row inspection does not supersede Nexamp’s Technical Specifications. Company will require the Contractor to change array installation/wire management techniques during construction to ensure approved “Golden Row” Specifications are met.

- Contractor shall be responsible for receiving and unloading all Company provided materials delivered to the Project Site for the electrical scope.

- Contractor shall inventory all Company provided material and shall assume responsibility for same once delivered. Contractor shall report any inventory variances or deficiencies upon 24 hours of delivery, after which point Contractor will be responsible for any future material shortages.

- Contractor shall be responsible for the installation of all trenching per the Project plans and specifications.

- Contractor shall provide road plates as required for crossing of trenches.

- Contractor shall provide temporary fencing as required for trenching.

- Contractor shall prepare, form, and pour all equipment pads. Contractor shall receive approval from Nexamp prior to pouring equipment pads.

- Contractor shall be responsible for providing all soil and concrete third-party testing at their sole cost in accordance with the Project Drawings and civil specifications and shall submit all test results to Nexamp for approval.

## Medium Voltage Services and Materials (applies to MV/Electrical scope only)

Contractor will assemble, construct, and install with its own forces and/or with Lower-Tier Subcontractors the following Work in accordance with the Project and Subcontractor Agreements.

Contractor to provide the following, but not limited to, material that is UL and 2017 NEC compliant or as specified in the drawings.

Contractor to perform the following services which is supplementary to and should be considered inclusive within the F&I schedule:

- Contractor shall provide all poles, conductors, and equipment, in accordance with attached F&I schedule.

- Contractor is responsible for installing all overhead electrical materials, equipment, and grounding.

- Contractor is responsible for installing all underground medium voltage conductors, and conduit between the poles according to the drawings for communications, etc. MV conduit from transformer to riser pole to be installed by electrical contractor.

- Contractor is responsible for all medium voltage terminations, including but not limited to terminations inside of the transformer, auxiliary transformer, grounding equipment, switchgear, etc.

- Contractor shall install and wire all medium voltage monitoring devices, including but not limited to current transformers, power transformers, and real-time automation controllers.

- Contractor is responsible for conducting very low frequency testing and ground testing of poles with equipment/grounding grids.

- Contractor shall correctly torque all such equipment or assemblies requiring torque, and mark torqued bolts to designate status of having been torqued. Failure of a bolt having been marked and designated as torqued may require all assemblies to be re-torqued in the presence of a Company Supervisor, if Contractor fails to remedy within seventy-two (72) hours. Nexamp reserves the right to source a third party to meet torquing requirements for which the Contractor will be held responsible for costs incurred if Contractor fails to remedy within seventy-two (72) hours after written notice.

- Contractor shall perform the installation and construction in accordance with all manufacturers’ requirements, installation manuals, and design Drawings in order to comply with the requirements for the maintenance of all warranties set forth in the Exhibits P and Q of the Project Agreement, respectively.

- Contractor is responsible for all rigging and logistics necessary to get all materials and equipment into place.

- Contractor is responsible for any temporary lighting, temporary power, extension cords, barriers, fall protection, or other means necessary to meet OSHA and Nexamp safety standards to provide a safe and satisfactory work environment.

- Contractor is responsible for coordinating inspections by any AHJ having jurisdiction over the Project, to obtain final permit inspection and sign-off.

- The provision of final redline As-built Drawings upon Guaranteed Completion Date.

## Fencing Services and Materials (applies to fencing scope only)

- Contractor shall be responsible for surveying the fence layout.

- Contractor shall furnish and install all fencing and related parts per the Drawings.

- Contractor shall take all precautions possible to not damage new plantings by the civil/landscape contractor, if any.

- Contractor shall ensure that posts are not “mushroomed” or have excessive splits that materially impact the posts integrity. All posts will be inspected by Nexamp QA/QC and may require replacement if found defective or damaged.

- Contractor is responsible for any damage to silt fence or other SWPPP measures.

- Contractor shall ensure that they do not go beyond the limits of disturbance for the site.

## Landscaping Services and Materials (applies to landscape scope only)

- Contractor shall be responsible for planting trees, shrubs, and/or live wetland staking as outlined in the Drawings.

- All conditions as outlined by the AHJ shall be observed, including but not limited to documents listed in Procore/Docs/Subcontractor/Permits.

## Company Provided Services and Materials

- Stamped electrical, structural and/or required design, engineering, and installation Drawings including Site plans.

- Design of site control for layout of Contractor's Work. Company will provide surveying for resource areas only.

- Detailed Site layout and design including as applicable geotechnical reports, civil engineering, drainage plan, grading plan, ground cover, and landscaping plan.

- Project management oversight.

- Company will work in conjunction with Contractor to facilitate the interconnection.

- Commissioning tests and procedures, with final commissioning to be performed by the Company’s technicians, and pre-commissioning to be performed by Contractor’s licensed electricians.

# Other Contractor Requirements

## Quality Control

- Contractor shall provide a QA/QC plan and provide a Site QA/QC Manager. The person performing the function of the Site QA/QC Manager may perform other functions in connection with the Work, provided that if Company or Owner observes any material deficiency in the quality of the Work, Company or Owner may require that Contractor provide (at no cost to Company) a full-time person to be the Site QA/QC Manager, who shall perform no other function in connection with the Work.

## Contractor Project Contacts

- Contractor is required to have a Project Manager to attend weekly Site production meetings.

- Prior to the commencement of any Work hereunder, Contractor shall provide Company and Owner with contact information for all lead individual(s) at the Project Site, including the titles, names, emails, and phone numbers of such individuals.

## Project Site Access and Security

- Company will provide Contractor with access to the Project Site as needed by Contractor for the provisions of the Services and the construction of the Project.

- Contractor agrees to not permit or bring anything onto the Site which is prohibited by or will in any way conflict with any legal requirements or which is prohibited by the standard form of fire insurance policy. This includes any materials or actions which will in any way increase the existing rate of or otherwise affect fire or any other insurance on the Site or any of its contents. Contractor agrees to not plan or bring Hazardous Material to the Project Site without first receiving Company’s explicit written approval.

## Work Plan and Schedule

- Contractor shall complete a written work plan for review and approval by Company and Owner. The work plan shall include access, mobilization, crane or lifting equipment, traffic control, methods of installation, staffing on week-by-week basis, and a clearly drawn working plan of the Project Site, including material storage, lay-down utilization, layout yard, Project Site office, and schedule.

- The Company shall have the option and the ability to add additional Nexamp Management and supplemental labor and/or equipment after a 72-hour written notification in order to maintain the schedule milestones. Nexamp shall pay Contractor for the accepted Services performed on a reduced scope of work. Contractor shall include as deductions in the reduced scope of work additional Nexamp Management on a Time and Material rate and the cost for the supplemental labor and/or equipment.

- Project Manager:		$150.00/hour

- Project Engineer:		$150.00/hour

- Construction Supervisor:	$125.00/hour

- Administrative Support:  	$75.00/hour

## Inspection

- Contractor shall notify Company at least twenty-four (24) hours prior to required construction inspections for scheduling purposes.

## Material Receiving, Handling, Inventory & Reporting

- Contractor shall maintain control of all its own material inventories at the Project Site.

- All materials shall be stored in an orderly fashion to prevent damage, facilitate proper inventory control, and maintain the appearance of a clean Project Site.

- Contractor shall be responsible for fully inspecting shipments for damage and shall report damage to both the manufacturer and Company in writing.

- Contractor shall be responsible for all material breakage and other damage occurring prior to Mechanical Completion caused by Contractor or its Lower-Tier Subcontractors.

- Contractor shall be responsible for all damage to Owner’s facility and property caused by Contractor or its Lower-Tier Subcontractors.

- Contractor shall maintain all equipment per manufacturer recommendations and as instructed by Nexamp.

- Contractor shall record received material by serial number, make, and model, and report weekly to Nexamp in writing. The report shall include the electronic submission of all receiving documents weekly.

- Contractor shall be responsible for maintaining and, if requested, providing to Company and Owner:

  - A daily diary with weather and number and type of employees on Site;

  - Bi-monthly Project Schedule updates and status reports; and

  - Weekly progress photos maintained electronically.

- All such reporting:

  - Shall be conducted via phone conference, e-mail, or in person at a pre-designated location and time.

  - Shall include, at a minimum, status to schedule, milestone completions, items inhibiting success/schedule, budget status, requests for changes, and any other problems inhibiting the completion of the Work; and

  - ANY UNAUTHORIZED OR UNPLANNED DAMAGE TO OWNER’S FACILITY SHALL BE REPORTED IN WRITING WITHIN TWENTY-FOUR (24) HOURS, WITH PHOTOGRAPHS.

## Safety

- Contractor shall provide a Site-specific Environmental Health and Safety Plan (the “Safety Plan”) and shall provide an onsite Environmental Health and Safety Manager. The person performing the function of the on-Site Environmental Health and Safety Manager may perform other functions in connection with the Work, provided that if Company or Owner observes any material safety deficiency in connection with the Work, Company or Owner may require Contractor to provide (at no cost to Company) a full-time person to be the on-Site Environmental Health and Safety Manager, who shall perform no other function in connection with the Work.

- Prior to beginning Work, Contractor shall provide Company with a copy of Contractor’s and any Subcontractor’s Safety Plan as well as an evaluation and appropriate documentation of the safety record of any licensed Contractor or Lower-Tier Subcontractor that will be performing Work on the Project. Company shall provide Owner with a copy the Safety Plan. Contractor and any Lower-Tier Subcontractors shall comply with any safety requirements in the EPC Contract, the Subcontractor Agreement, Project Agreement, and all applicable federal, state, and local safety laws.

- Safety Plan Implementation.

  - Contractor shall conduct daily job hazard analysis meetings to identify and mitigate potential work hazards prior to beginning Work.

  - Contractor shall conduct environmental health and safety orientation for any new personnel prior to their being released to Work on the Site.

  - Contractor shall provide regular written operating reports to Company, including Plan of the Day reports, weekly reports, and monthly reports.

  - Contractor shall convene all-hands safety meetings once a week, or more frequently, if necessary, attended by all Contractors and its Lower-Tier Subcontractors employees on the Project Site. Attendance at these meetings shall be mandatory. Printed names shall be taken of those attending the meeting and provided to Nexamp upon request. No individual may start Work on the Project Site without having attended a safety briefing on the dangers and protocols of the Project Site.

  - No individual will operate a piece of equipment on which such individual has not had certification training. Certification shall be carried on the operator at all times while operating the applicable piece of equipment.

  - Contractor, at a minimum, shall have a mandatory pre-job safety briefing for all employees and its Lower-Tier Subcontractor employees on their first day on the Project Site. Hardhat stickers, or the equivalent, shall be issued as a proof of briefing attendance.

  - Contractor shall maintain the Project Site in a clean and orderly condition, generally free of litter and debris to ensure it is presentable to the Owner, the Host, the tenants, and the public, including news media and members of the general public.

  - Contractor shall ensure that all permanent, temporary, and subcontracted personnel are provided with, are trained to use, and are using, appropriate personal protective equipment and safety equipment as necessary to execute the Work in a safe and workmanlike fashion. Safety vest, hardhats, and safety glasses shall be worn at all times.

  - Contractor shall provide additional safety apparel for unexpected visits from Company or its representatives. This will include five (5) hard hats, five (5) safety glasses, and five (5) safety vests. No unscheduled visits or tours on an active construction Site.

  - All ladders shall be of non-conductive glass reinforced plastic construction and shall be in good condition.

  - ALL Employees on the job Site shall have at minimum OSHA 10hr Certification and must be able to present proper licensure when requested.

## Documentation

- Contractor shall maintain the following documentation at the Project Site:

  - One (1) copy of the construction drawings and one (1) copy of redlined Drawings marked as “as-built” Drawings, to be retained by Contractor. Weekly as-built Drawings redlines are required.

  - The latest version of the Project Schedule.

  - Hard and Digital Copies of all Change Orders.

  - Hard and Digital Copies of the Safety Plan.

  - Hard and Digital Copies of any revisions or modifications to the Project Agreement.

  - Any other documentation required by applicable law.

## Fire Prevention

- Contractor shall provide an adequate number of fire extinguishers as appropriate for the Project Site. These fire extinguishers must be charged, with a current tag, in good order, and of a type appropriate for the fire risks that may reasonably be anticipated. The number and type must fulfill the requirements of any and all state and local codes.

## Severe Weather

- Contractor acknowledges that the Work may entail direct exposure to severe weather which may in extreme circumstances result in Project Schedule delays.

- Severe Weather is defined as:

  - The daily minimum high temperature is less than twenty-five (25°) degrees Fahrenheit.

  - Snow accumulation is greater than four (4) inches during a single event.

  - Rain accumulation is greater than two (2) inches during regular working hours.

  - Working temperature greater than one hundred (100° F) degrees Fahrenheit on the ground.

  - Sustained winds greater than 20 mph for one (1) hour or more.

- Weather shall be recorded from nearest weather station, as defined by the conditions at Frederick, IL, www.weather.gov.

- If Contractor is impacted by severe weather, Contractor shall as soon as reasonably possible, but in no event more than five Business Days thereafter, provide written notice supported by historical weather data to the Company of the circumstances involved in the delay and follow the Force Majeure Event procedure set forth in the Subcontractor Agreement.

## Winter Conditions Contingency

Contractor shall immediately notify Client of any “Winter Conditions” (as defined below) that may impact the Project Schedule. At the option of Client, in the event of Winter Conditions, either (i) each outstanding “Finish” date listed in the latest Procore schedule provided by the Project Manager will be extended on a day-for day basis for each day of Winter Conditions, or (ii) the Contract Price shall be adjusted to reflect reasonable, documented out-of-pocket costs incurred by the Contractor in order to continue performing on schedule during the Winter Conditions.  At the request of Client, Contractor shall provide documentation or data substantiating the Winter Conditions. Notwithstanding anything herein to the contrary, in no event shall the Contract Price adjustment for Winter Conditions exceed the predetermined amount.

“Winter Conditions” means unusually severe weather conditions for the location of the Site, provided that weather shall only be considered severe if the daily minimum high temperature is less than 25 degrees, snow accumulation is greater than 4 inches during a single event, rain accumulation is greater than 2 inches during regular working hours, and/or winds are greater than 20 miles per hour for one or more hours. Contractors shall make up days to maintain schedule if not within this standard.

# Company Contacts

Key Members of Nexamp’s Deployment Team:

Robert Walsh

Construction Program Manager

Robert Walsh@nexamp.com

(518)487-0411

Betsy Thomas

Project Manager

BThomas@nexamp.com

(309)361-0559

Denice Hallstein

Construction Manager

DHallstein@nexamp.com

(802)380-0810

(Pending)

Site Senior Superintendent

@nexamp.com

Phone #

(Pending)

Site Superintendent

@nexamp.com

Phone #

Jasmine Bracero

Construction Project Coordinator

JBracero@nexamp.com

# Exhibit 1. Furnish & Install (F&I) Schedule

Nexamp to provide the following materials:

| Description | Furnished By | Installed By |
| --- | --- | --- |
| Photovoltaic Modules | Nexamp | Module/Mech. Contractor |
| Mounting |  |  |
| Foundation | Nexamp | Foundation/Mech. Contractor |
| PV Rack | Nexamp | Racking/Mech. Contractor |
| PV Racking Legs | Nexamp | Mechanical Contractor |
| BOS Equipment |  |  |
| Switchgear | Nexamp | Electrical Contractor |
| Combiner Boxes/ String Inverters | Nexamp | Electrical Contractor |
| Recloser (Tavrida OSM, 15KV, Schweitzer SEL 651R, Lindsey Sensors w/ CTs) | Nexamp | Electrical Contractor |
| Transformers | Nexamp | Electrical Contractor |
| DC Wire | Electrical Contractor | Electrical Contractor |
| Data Acquisition System (DAS) |  |  |
| Fully Integrated DAS Cabinet | Nexamp | Electrical Contractor |
| Cameras (if applicable) | Nexamp | Electrical Contractor |
| Weather Stations | Nexamp | Electrical Contractor |
| Electrical Materials |  |  |
| Array Wiring Materials (PV connectors, jumpers, zip ties, edge guard, etc.) | Electrical Contractor | Electrical Contractor |
| AC Wiring Materials (conduits, supports, junction boxes, handholes/manholes, etc.) | Electrical Contractor | Electrical Contractor |
| MV Underground Conductor and Equipment | Electrical Contractor | Electrical Contractor |
| MV Overhead Conductor and Equipment | Electrical Contractor | Electrical Contractor |
| Grounding Materials (grounding wire, rods, and bonding) | Electrical Contractor | Electrical Contractor |

Contractor to furnish and install all electrical equipment not listed in the above F&I table that is required to complete the electrical scope of work to code, based on the construction drawings included in the contract.

# Exhibit 2. Execution Plan

| Please provide execution plan. |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MS Project is acceptable. |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Total Days Mobilize to Complete |
| Dates: |  |  |  |  |  |  |  |  |
|  | Week 1 | Week 2 | Week 3 | Week 4 | Week 5 | Week 6 | Week 7 |  |
| Civil Contractor |  |  |  |  |  |  |  |  |
| Mobilize |  |  |  |  |  |  |  |  |
| ECB installed |  |  |  |  |  |  |  |  |
| Clearing and Grubbing |  |  |  |  |  |  |  |  |
| Site roads |  |  |  |  |  |  |  |  |
| Grading |  |  |  |  |  |  |  |  |
| Storm Water Management |  |  |  |  |  |  |  |  |
| Fence Installation |  |  |  |  |  |  |  |  |
| Foundation Contractor |  |  |  |  |  |  |  |  |
| Mobilize |  |  |  |  |  |  |  |  |
| Survey |  |  |  |  |  |  |  |  |
| Installed |  |  |  |  |  |  |  |  |
| Punch List |  |  |  |  |  |  |  |  |
| Mechanical Contractor |  |  |  |  |  |  |  |  |
| Mobilize |  |  |  |  |  |  |  |  |
| Racking Installation |  |  |  |  |  |  |  |  |
| Module Installation |  |  |  |  |  |  |  |  |
| Punch List |  |  |  |  |  |  |  |  |
| Electrical Contractor |  |  |  |  |  |  |  |  |
| Mobilize |  |  |  |  |  |  |  |  |
| Install Conduit |  |  |  |  |  |  |  |  |
| Install Pad |  |  |  |  |  |  |  |  |
| Build String Inverter Racks |  |  |  |  |  |  |  |  |
| Pull Wires/Feeders |  |  |  |  |  |  |  |  |
| Install equipment |  |  |  |  |  |  |  |  |
| Wire Equipment |  |  |  |  |  |  |  |  |
| Wire Management |  |  |  |  |  |  |  |  |
| MV Work |  |  |  |  |  |  |  |  |
| Commissioning Testing |  |  |  |  |  |  |  |  |
| Red line drawings |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Total Days Mobilize to Complete |
| Dates: |  |  |  |  |  |  |  |  |
|  | Week 1 | Week 2 | Week 3 | Week 4 | Week 5 | Week 6 | Week 7 |  |

| 3. Please fill in below the name of each Lower-Tier Subcontractor, define the scope of work and populate the table with the assumed manpower totals for each week. |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Manpower |  |  |  |  |  |  |  |
|  | WK 1 | WK 2 | WK 3 | WK 4 | WK 5 | WK 6 | WK 7 |  |
| Civil Contractor | (Self-Performing Scope) |  |  |  |  |  |  |  |
| Management |  |  |  |  |  |  |  |  |
| Foreman/Journeyman |  |  |  |  |  |  |  |  |
| Labor |  |  |  |  |  |  |  |  |

# Exhibit 3. Alternate and Unit Price (as applicable to your scope only)

All unit pricings are to assume the material delivery is included and the material placement will require no additional mobilizations.

| Bid Item | Unit Prices | Unit |
| --- | --- | --- |
| Ledge Removal |  | Cu yd |
| Borrow Gravel |  | Ton |
| Loam |  | Ton |
| 3"-6" Trap Rock |  | Ton |
| 4"-6" Trap Rock |  | Ton |
| Conservation Mulch |  | Ton |
| Arborvitae |  | EA |
| Straw bale Check Dam |  | LF |
| Silt Fence |  | LF |
| Straw bales |  | LF |
| Wattles |  | LF |
| Hydro seed |  | $/ACRE |
| SWPPP Contingency |  | Lump Sum |
| Mowing of Staging Area |  | Lump Sum |
| Bedding Sand |  | Lump Sum |

# Exhibit 4. Bid Quantity Breakout (as applicable to your scope only)

| Bid Item | Quantity | Unit |
| --- | --- | --- |
| Ledge Removal |  | Cu Yd |
| Road |  | LF |
| Arborvitae |  | Each |
| 3"-6" Trap Rock |  | Ton |
| 4"-6" Trap Rock |  | Ton |
| Straw bale Check Dam |  | LF |
| Silt Fence |  | LF |
| Straw bales |  | LF |
| Wattles |  | LF |
| Hydro seed Fall |  | Acres |
| Hydro seed Spring |  | Acres |
| Trench - DC |  | LF |
| Trench - AC |  | LF |
| Stormwater Detention System |  | LF |

# Exhibit 5. Owner Provided Equipment Schedule

| Equipment | PO Number | Estimated Ship Date |
| --- | --- | --- |
| Racking / Foundation | 20610 | Available (Nexamp Warehouse) |
| Combiner Box | 20297 | Available (Nexamp Warehouse) |
| String Inverter | 20089 | Pending Date |
| Central Inverter | N/A | N/A |
| Gang Operated Load Break | 20775 | Available (Nexamp Warehouse) |
| DAS Enclosure | 22463 | Available (Nexamp Warehouse) |
| CT-PT-PMU | 20849 | Available (Nexamp Warehouse) |
| DAS Components | 22268 | Available (Nexamp Warehouse) |
| Switchgear | 20324 | Available (Nexamp Warehouse) |
| Transformer | 20237 | Available (Nexamp Warehouse) |
| Yellowjackets | N/A | N/A |
| Recloser | 20774 | Available (Nexamp Warehouse) |

As of 03/19/2026